# DI Cooling Skid Process Control Narrative

| Prepared By NOAH OVIKIAN | Prepared Date 9/6/2026 |
| --- | --- |
| Reviewed By ETHAN HENDERSON | Review Date |
| Approved By | Approval Date |

Contents

1.	Introduction	3

1.1. Purpose	3

1.2. Control Philosophy	3

2.	System Operation	3

2.1. System Off	3

2.2. System Initialization	3

2.3. System Calibration	4

2.4. System Active	4

2.5. System Shutdown	4

2.6. Fault Management	4

3.	Temperature Control	5

3.1. Signal Processing	5

3.2. Temperature Regulation	5

3.3. Manual Operation	6

4.	Hydraulic Control	7

4.1. Signal Processing	7

4.2. Low Thresholds & Failure Classification	7

4.3. Hydraulic Failure Pump Turnover	8

4.4. Lifecycle Pump Turnover	8

4.5. Manual Operation	9

5.	Vessel Level Control	9

5.1. Signal Processing	9

5.2. Level Monitoring	10

5.3. Redundancy Control	10

6.	Conductivity Control	10

6.1. Signal Processing	10

6.2. Conductivity Monitoring	10

6.3. Redundancy Control	11

# Introduction

## Purpose

The purpose of this document is to describe process, methods and philosophy for controlling the DI VFD Cooling Skid for the Toshiba-Mitsubishi Industrial Electric Corporation (TMEIC). This document shall act as the primary method of communication when describing the process, methods, and philosophy of skid control, serving to align all parties and entities involved in the engineering, procurement, construction, and operation of the cooling skid. All changes to the process, methods and philosophy of control of the cooling skid, shall be formalized through this document.

## Control Philosophy

This DI cooling skid shall act as model for the DI cooling skid responsible for cooling TMEIC’s Variable Frequency Drive. The three primary control objectives of this skid is to ensure that VFD is supplied with coolant which does not surpass a temperature of 45°C, that coolant supplied to the VFD is uninterrupted, that coolant conductivity never surpasses 1 μS/cm at 25°C, and that pumps installed within the system are not damaged.   Additionally, it shall be assumed that ambient air temperatures shall not exceed 35°C.

# System Operation

## System Off

When the system is off, neither the primary nor secondary pump shall be active. The 3-way valve shall be actuated to be 100% open. Temperature and Hydraulic Controls shall be disengaged, while vessel level controls and conductivity controls shall always be engaged.

## System Initialization

System initialization shall occur when the system is started by the user by engaging the system start switch (SW-1) or shall occur when the system experiences a pump turnover, either manually or automatically. The initialization stage shall last for 15 seconds before the system moves into the calibration stage. During system initialization, temperature and hydraulic controls shall be disengaged, to allow for adequate pressure, and flow to build within the system. During initialization the 3-way valve shall be 100% open.

## System Calibration

The system shall always reach the calibration stage after the initialization stage. The calibration stage shall last for 5 seconds before the system moves into the active stage. During system calibration, hydraulic controls shall be enabled, and temperature controls shall be partially enabled, allowing for the 3-way valve to adjust to appropriate position based on the input temperature without tripping the temperature alarm or fault signals. This will allow for the system to align correctly with the system temperature at proper pressure and flow.

## System Active

The system shall reach the active stage after the calibration stage. In the active stage, all controls are fully enabled, and the skid is considered to be in normal operation.

## System Shutdown

The system shall enter the shutdown stage should there exist any fault (that is any FLT-X is engaged where X is any integer), or should the operator engage the system shutdown switch (SW-2). The shutdown stage shall last for 10 seconds before entering the off stage. Hydraulic controls and temperature controls shall be disengaged throughout system shutdown, and the 3-way valve shall be 100% open.

## Fault Management

If there is any fault within the system during operation (that is, any FLT-X is engaged, where X is any integer), then the system shall enter the shutdown stage, regardless of the stage it is currently in. Should any fault exist while the system is in the off stage, the system shall not enter the initialization stage when the operator starts the system. If the operator engages the acknowledge fault switch (SW-14), all faults shall be disengaged and the acknowledge fault switch shall disengage. If the operator engages the start switch after engaging the acknowledge fault switch, the system shall enter the initialization stage. The acknowledge fault switch only disengages fault, hence an existing fault within the system shall always reengage the respective fault if not properly handled by the operator.

# Temperature Control

## Signal Processing

Inlet coolant temperature (SIG-6) shall be sampled prior to entering the heat source, and just after exiting the heat-exchanger loop. 3 RTD sensors (P15) shall be used in determining the measured coolant temperature. RTD sensors shall communicate to the PLC using a 4-20 mA INT-valued signal (PHY-2, PHY-3, and PHY-4 respectively). Any RTD signal that exceeds 20.5 mA or falls below 3.5mA shall be considered a bad signal, and the affected RTD shall be considered as “non-functioning” and shall engage the respective alarms (ALM-14, ALM-15, ALM-16). All INT-valued signals from the RTDs shall be converted into REAL-valued signals (SIG-10, SIG-11 SIG-12 respectively). If 3 of 3 sensors are functioning, the median value of the REAL-valued RTD signals shall be considered as the measured coolant temperature (SIG-6). If 2 of 3 sensors are functioning, the average value of the 2-functioning REAL-valued RTD signals shall be considered as SIG-6. If less than 2 of 3 sensors are function, FLT-7 shall be engaged, and the last read measured coolant temperature shall be considered as SIG-6 for measurement continuity during system shutdown.

The measured coolant temperature shall be regulated by controlling flow entering the heat exchanger through a 3-way electrically actuated valve (P2). Valve open percentage shall be stored as a REAL-valued signal (SIG-9), which will be converted into a WORD-valued 4-20mA output signal for valve actuation (PHY-16)

## Temperature Regulation

A multi-stage control scheme shall be implemented, in which P2 shall be actuated to direct 0%, 25% 50% 75% or 100% of the total flow through the heat exchanger. (Percentage of total flow through the heat exchanger shall henceforth be called throughput flow). Throughput glow shall be directly proportional to the open percentage of the valve. Additionally, the heat exchanger itself shall be fitted with two pairs of fans to assist with convection cooling. These fans shall be controlled binarily through a digital 0-24V signal (PHY-12, PHY-13). When throughput flow is greater than 0%, both pairs of fans shall be activated, and when throughput flow is at 0%, both pairs of fans shall be deactivated.

Table 1 shows the relationship between measured temperature, throughput flow, valve open percentage, and fan control.

Table 1: List of Temperature Ranges correlating throughput flow, valve position, and fan actuation

| Temperature (T) | Throughput Flow % | Valve Open % | Fan Actuation |
| --- | --- | --- | --- |
| T ≤ 35°C | 0% | 0% | OFF |
| 35°C < T ≤ 38°C | 25% | 25% | ON |
| 38°C < T ≤ 41°C | 50% | 50% | ON |
| 41°C < T ≤ 44° C | 75% | 75% | ON |
| T > 44°C | 100% | 100% | ON |

Temperature regulations shall have hysteresis control, where a change in throughput flow and fan actuation requires temperature to remain within a new region for at least 2 seconds.

Should the measured coolant temperature reach or surpass 44°C and remain at that level for a duration of at least 10 seconds, a high coolant temperature alarm (ALM-1) be engaged. At any point where ALM-1 is engaged, should the measured coolant temperature fall below 44°C, ALM-1 should be disengaged. Should the measured coolant temperature reach or surpass 45°C but fall below 44°C before 5 seconds has elapsed, ALM-1 shall remain disengaged.   Should the measured coolant temperature reach or surpass 45°C, ALM-1 shall be engaged, and shall only be disengaged once the measured coolant temperature falls below 44°C. Should the measured coolant temperature reach 45°C and remain at 45°C for at least 5 seconds, the system shall engage the temperature fault (FLT-1), and the system shall shutdown. Should the measured coolant reach 45°C but fall below 45°C before 5 seconds elapse, FLT-1 remain disengaged.

## Manual Operation

P2 and each fan pair may be manually controlled by the operator if and only if the respective manual control override switch (SW-5 & SW-6) has been engaged. Should SW5 and/or SW6 be engaged the operator may engage or disengage the fans using switches SW-8 and SW-9 for fan 1 and 2 respectively. Likewise, should the operator engage SW-6, the operator may actuate the valve on or off at any point during system operation using switch SW-7. Note that engaging SW-5 shall enable the automatic valve control disabled alarm (ALM-11) and engaging SW-6 shall engage the automatic fan control disabled alarm (ALM-12)

# Hydraulic Control

## Signal Processing

System hydraulics shall be observed by three parameters: pump power, flow, and pressure. Pump power shall be communicated from the active pump (P1A/P1B) to the PLC through a 4-20mA WORD-valued signal. Specifically, the primary pump power shall be communicated through WORD-valued signal PHY-5 and the secondary pump power shall be communicated through WORD-valued signal PHY-6. A pump power signal that exceeds 20.5 mA or falls below 3.5 mA shall be considered a bad signal, engaging ALM-7 or ALM-8 (respective of the pump). The WORD-valued signals of the primary and secondary pumps shall be converted into a REAL-valued signal (SIG-13, and SIG-14 respectively). Only the power of the active pump shall be considered as the measured pump power (SIG-5). Flow shall be sampled by an ultrasonic flowmeter (P13) and communicated to the PLC through a 4-20mA WORD-valued signal (PHY-1). A flow signal that exceeds 20.5 mA or falls below 3.5 mA shall be considered a bad signal, engaging alarm ALM-13. The WORD-valued flow signal shall be converted into a REAL-valued signal (SIG-8)   System pressure shall be observed binarily as to be low or nominal. System pressure status shall be communicated to the PLC through a 0-24V signal (PHY-17). System pressure shall be passed through a hysteresis filter before being considered as the final pressure measurement (SIG-16 and SIG-22)

Primary and secondary pumps shall be engaged using a 0-24V signal from the PLC (PHY-14, PHY-15). One and only one pump may be active during the operation. A pump is considered active if it receives a 24V signal from the PLC.

## Low Thresholds & Failure Classification

Pump power shall be classified binarily as either low or nominal. Pump power that reaches or drops below 500 Watts shall be classified as low. Pump power that exceeds 500 Watts shall be considered nominal. Flow shall be classified binarily as either low or nominal. Flow that reaches or drops below 3.5 GPM shall be considered low. Flow that exceeds 3.5 GPM shall be considered nominal.

Additionally, should the active pump power signal or the flow signal be considered bad, the pump power and/or the flow signal shall be automatically classified as low.

The state of the system’s hydraulics shall be binarily determined as either nominal or failed. Additionally, the system’s hydraulics shall be dependent on the pump driving it. That is, for a primary and secondary pump, the system shall have primary and secondary hydraulics. The system’s primary hydraulics are considered to have failed if and only if any 2 of the 3 hydraulic parameters are considered low, whilst the primary pump is active. A primary hydraulic failure shall enable ALM-9 The system’s secondary hydraulics are considered to have failed if and only if any 2 of the 3 hydraulic parameters are considered low, whilst the secondary pump is active. A secondary hydraulic failure shall enable alarm ALM-10 In the event of a primary or secondary hydraulic failure, the system will attempt an automatic pump turnover. During system initialization, a system’s hydraulics status shall be overridden as nominal.

The primary and secondary hydraulic failures may be only disabled by the operator by enabling the acknowledge hydraulic fault switches (SW-10 and SW-11 respectively)

Power, pressure and flow classifications shall be fitted with hysteresis control, such that a change in classification (that is, a change from nominal to low or from low to nominal), must meet the threshold requirements listed above for at least 2 seconds.

## Hydraulic Failure Pump Turnover

The primary and secondary pumps shall not be active at the same time.  All pumps will remain off while the system is not running, or the system is shutting down. The system may run in duplex mode, in which the simplex mode switch (SW-3) is disengaged, or in simplex mode, in which the switch is engaged. When the system changes from off to initialization, the primary pump shall always be activated. Should a hydraulic failure occur in connection with the active pump, the system should attempt an automatic pump turnover. Should the simplex switch be engaged in the event of an automatic pump turnover, the system will engage the duplex failure fault (FLT-6) and shutdown. Should the simplex switch (SW-3) be disengaged during the event of an automatic pump turnover, the active pump shall receive 0V signal from the PLC, and the current non-active pump shall receive a 24V. The system will then automatically engage the simplex switch (SW-3). Only the operator may disengage SW-3 at any point during skid operation.

## Lifecycle Pump Turnover

To maximize the lifespan of the primary and secondary pump, the cooling skid shall have an automatic lifecycle pump turnover feature. Pump turnover for the pump lifecycle shall be henceforth called pump cycling. Pump cycling may only occur should the enable pump cycling switch (SW-12) be engaged. While the simplex mode switch is engaged, the enable pump cycling switch shall always be disengaged. While the simplex mode switch is disengaged, the operator may choose to engage or disengage the pump cycling switch during skid operation.

The primary and secondary pump differential usage shall be counted using hours (i.e. ticks in the program), by a LINT-valued differential pump signal (SIG-25) Primary pump usage shall increase SIG-25 by 1 for every hour in operation. Secondary pump usage shall decrease SIG-25 by 1 for every hour in operation.

Should pump cycling be engaged, and the pump differential signal reach or surpass 168, and the primary pump is active, an automatic pump turnover shall be initiated, in which the secondary pump shall receive a 24V signal from the PLC and the primary pump shall receive a 0V signal from the PLC. Should pump cycling be disengaged, and the pump differential signal reach or surpass 168, and the primary pump is active, the pump cycle alarm (ALM-17) shall be engaged. Should pump cycling be engaged, and the pump differential signal reach or pass below -168 and the secondary pump is active, then an automatic pump turnover shall be initiated, in which the primary pump shall receive a 24V signal from the PLC and the secondary pump shall receive a 0V signal from the PLC. Should pump cycling be disengaged, and the pump differential signal reach or pass below -168, the pump cycle alarm shall be engaged.

The operator may choose to reset the pump differential signal to 0 at any point during skid operation by engaging the Reset Pump Differential Switch (SW-13).

Should the pump differential signal reach 263 – 2 or -263 + 1 the overflow/EOTW fault (FLT-8) shall be engaged, and the system shall shutdown

## Manual Operation

The operator may choose to engage SW-3 at any point during skid operation. The operator may choose to attempt a manual pump turnover at any point during operation by engaging the manual turnover switch SW-4. Should SW-3 be engaged when attempting to engage SW4, SW4 shall disengage with no additional action. Should SW3 be disengaged when attempting to engage SW-3, SW-4 will disengage, and a pump turnover shall commence, in which the current active pump receives a 0V signal from the PLC, and the current inactive pump receives a 24V signal from the PLC

# Vessel Level Control

## Signal Processing

The vessel storing excess coolant shall be fitted with two hall sensor switches to indicate low coolant level in the vessel (P17A) and critical low coolant level in the vessel (P17B). These hall sensors shall be engaged if the coolant level within the vessel falls below the level at which the respective sensors have been installed on the vessel. The hall sensors shall be disengaged when the coolant level within the vessel is at, or surpasses, the level at which the hall sensors have been installed at.

Both hall sensors shall be integrated with hysteresis control, such that the physical signals (PHY-10 and PHY-11 respectively), shall not engage the final output signals (SIG-20, SIG-21) until at least 500 milliseconds have elapsed

## Level Monitoring

If SIG-20 is engaged, the Low Coolant Level in Vessel Alarm (ALM-2) shall be engaged. If both SIG-20 and SIG-21 are engaged, the critical vessel level fault (FLT-2) shall be engaged, and the system shall shut down.

## Redundancy Control

Should SIG-21 be engaged, but SIG-20 remain disengaged, the Level Sensor Malfunction fault (FLT-4) shall engage, and the system shall shut down.

# Conductivity Control

## Signal Processing

The conductivity sensor shall communicate to the PLC using a 4-20mA WORD-valued signal (PHY-7). The WORD-valued signal shall be converted into a REAL-valued signal (SIG-7). Additionally, the conductivity sensor shall communicate integrated alarm and fault trips by communicating to the PLC through 0-24V BOOL-valued signal (PHY-8, PHY-9). The alarm and fault trip signals shall be passed through a Hysteresis filter, requiring 500mS of stability before engaging the filtered alarm and fault signals (SIG-23, SIG-24).

In addition to the alarm and fault trips in the conductivity sensor, the REAL-valued signal shall also be observed for the same alarm and fault conditions. The REAL-valued signal shall be passed through a hysteresis filter, requiring 500 ms of stability before its value is classified as an alarm or fault condition.

## Conductivity Monitoring

Should the conductivity sensor alarm trip, and the REAL-valued signals observe a conductivity at or greater than 0.9 μS/cm at 25°C, the conductivity alarm (ALM-3) shall be engaged. Should the conductivity sensor alarm trip, and the conductivity sensor fault trip, and the REAL-valued signal observe a conductivity greater than 1 μS/cm at 25°C, the critical conductivity fault (FLT-3) shall be engaged.

## Redundancy Control

Should the conductivity sensor fault trip engage while the conductivity sensor alarm trip remains disengaged, the conductivity sensor malfunction fault (FLT-5) shall be engaged.

Should the conductivity sensor alarm trip engage, but SIG-7 fails to observe a conductivity at or greater than 0.9 μS/cm at 25°C after an elapsed time of 2 seconds, FLT-5 shall be engaged. Should SIG-7 observe a conductivity at or greater than 0.9 μS/cm at 25°C, but the conductivity alarm trip fails to engage after an elapsed time of 2 seconds, FLT-5 shall be engaged. Should both the conductivity sensor alarm trip engage, and the conductivity sensor fault trip engage, but the SIG-7 fails to register a conductivity greater than 1 μS/cm at 25°C after an elapsed time of 2 seconds, FLT-5 shall be engaged. Should the conductivity fault trip fail to engage, regardless of whether the conductivity sensor trip alarm is, or is not engaged, while SIG-7 registers a conductivity greater than 1 μS/cm at 25°C after an elapsed time of 2 seconds, FLT-5 shall be engaged